1. Acceptable Manufacturers
	1. AAF Flanders
	2. Other Approved Manufacturer
2. Quality and Environmental Management Systems
	1. The manufacturer shall have an ISO 9000 or ASME NQA-1 quality based system at the manufacturing facility. The manufacturer shall make available documentation showing independent third party certification or acceptable audit approvals and adherence to these systems.
	2. If requested, manufacturer shall make available a copy of their Corporate Quality Manual and references from clients of similar sized projects or scope within the last 5 years.
3. AstroHood S-II Terminal Filter Modules Testing
	* + 1. Terminal Ducted Air Filter Modules shall be individually factory-tested and certified.
			2. Each hood shall have a serial number allowing for full traceability. Each hood shall be individually serialized and traceable to the specified leak test procedure.
			3. Certification of each HEPA filter in accordance with applicable IES Standard(s) and specifications indicated below. Each filter shall have permanent label indicating filter type, model number and size designator, unique serial number allowing for full traceability, air resistance, airflow, target efficiency, target pressure drop and test date, average penetration and probe test certification.
4. AstroHood S-II Construction
	* + 1. Fluid seal housing shall be constructed of 16 gauge 304 series stainless steel with joints and seams fully welded. Aluminum in equivalent thickness is available as an option. The housing is available to be white powder coated as an option. The assembly shall be able to withstand a positive or negative pressure of 3" w.g.
			2. Fluid Seal housing shall be constructed in a manner that includes a completely sealed integral knife edge to mate with the fluid seal trough on the filter and form a leak proof seal between housing and filter frame. Knife edge to be formed by bending side wall of housing and forming a sealing edge. Tack welding and caulked knife edges with potential leak points are not acceptable. Housing side wall shall be equipped with swirled factory predrilled hole to accept pop rivets for connection of the perimeter trim.
			3. Housing shall have round or square duct connection with crimped inlet collar intermittently welded and caulked into the hood body, size and type as shown on the Drawings or data schedules/data sheets. If needed, the unit can be specified with a side inlet of the same material as the hood body. The side inlet shall be square or rectangular and be continuously welded to housing.
			4. The unit shall come equipped with a factory installed guillotine damper as standard. The damper shall be operated by a mechanical rod linkage assembly of stainless construction with a control rod. Adjustment mechanism shall operate from full open to full closed position with a quarter revolution. The damper adjustment mechanism shall include a set screw to lock the damper position in place. The damper control mechanism shall be operable from room side. Butterfly and ESD dampers available as options.
			5. The housing shall have a validated aerosol injection system with a port located in knife edge of housing to inject an aerosol challenge into the manifold system of the guillotine damper accessible from air outlet side. The manifold system is designed to introduce test aerosol at the hood inlet for filter penetration testing. Aerosol distribution tubing shall be flexible tygon tubing. Aerosol uniformity upstream of the damper shall deviate no more than +/- 25% of the standard deviation when measured via traverse damper readings. Reports should be provided. The assembly shall have a 3/8” female NPT fitting as standard. Optionally a 3/8" chrome plated “Colder” quick disconnect fitting with a “BUNA-N” ring seals and snap-in barbed connector.
			6. There shall be a labeled test port, accessible from the air outlet side, to measure static pressure and upstream aerosol concentration at filter inlet upstream of filter but downstream of damper. The assembly shall have a 3/8” female NPT fitting as standard. Optionally a 3/8" chrome plated “Colder” quick disconnect fitting with “BUN-A” ring seals and snap-in barbed connector.
			7. The unit shall have hanging tabs on the top edge of housing at each of the 4 corners. They shall be plug welded to the housing. Other optional mounting methods are Mounting Pads and Clean Ceiling Angle either at two or three inches from the bottom of the unit. Pop riveted connections are not acceptable.
			8. Housings shall include filter alignment tabs welded in place to center the filter in the housing.
			9. Housing shall have four captive retainers to secure gel seal filters with knife-edge seal between housing and fluid-filled channel around perimeter of filter frame.
			10. If required, the entire housing shall be insulated at the factory with two inch thick, foil-backed, fiberglass insulation. Armoflex foam is an option to the fiberglass insulation. Insulation shall comply with requirements of ASTM E84, NFPA 255 and UL 723. Tape seams with aluminum foil backed tape.
			11. Grille shall be 20 gauge 304 or 316L stainless steel with No. 3 finish room side, perforated to provide 40% free area. The grille shall be flush and be installed with four 3/8” acorn nuts as standard. Optionally the grille shall be flush-mounted with stainless steel removable hinges on long side of housing and two quarter turn stainless steel hand operated fasteners, which do not require use of hand tools. Other options include 40% free area painted grille. The perforated grille is to have a hemmed edge for rigidity.
			12. The perimeter trim shall be non-removable unless field installed trim for hard/plaster ceilings is specified. Trim shall be 1/2” permanent, or 1/2” or 1-1/2” wide field installed trim constructed of minimum 18 gauge type 304 or 316L stainless steel with No. 3 finish on surfaces exposed to the room.
			13. All hoods shall be visually inspected for pinholes, porosity, indentations or inclusions exceeding 10% base metal; lack of filler material, excessive weld build up and cold shunts. Hoods shall be leak tested per manufacturer’s quality control procedure. QC procedure to be submitted for approval with product submissions. The hood knife edge shall be sealed off with a jig and the hood plenum area will be pressurized to 3.0” w.g. All exterior hood body weld, all welds in the filter sealing surface area and all penetrations such as damper control, static pressure and aerosol ports shall be bubble tested for leaks. All hoods must meet a zero leak criteria.
5. HEPA/ULPA Filters
	1. Filters construction shall be extruded anodized aluminum for use in open plenum systems, ducted terminal systems, or Fan Powered Systems. Frame style will be determined by filter application. The term “HEPA” shall be used generically to describe all high-efficiency filters that meet the following specifications. If possible, the filter and housing shall be from the same manufacturer to ensure form, fit, and function are maximized.
	2. Construction Criteria;
		1. The filter shall be constructed in accordance with the recommended construction requirements of IEST-RP-CC001, latest version.
		2. The HEPA filter media pack shall be constructed of a pleated single and continuous layer of fire resistant borosilicate micro-fiberglass. Pleats are to be equally spaced using hot melt media separators or glue coated media ribbons. Nominal media pack depth shall be 2”, 3”, or 4” deep.
		3. The media pack shall be affixed permanently to the filter frame assembly by means of a solid, continuous, fire retardant, phosphorous free polyurethane sealant, forming a leak free bond between the filter pack and filter frame. The sealant will be uniform off-white in color; will not exhibit any form of leaching, and no more than ¼” of wicking into the media. The sealant will be qualified at incoming inspection as well as point of dispensing to ensure homogenization and adequate curing and adhesion properties.
		4. The filter frame shall be of minimum of 0.060” thick webbing anodized extruded aluminum Filter Frame shall be designed for use in Fluid Seal systems. The filter frame shall have a perpendicularity specification of no more than 1% to ensure tight miter corners and a leak free design. Corners must contain no cracks or uneven areas.
		5. Fluid Seal system filters shall have:
			1. A continuous trough around the perimeter of the filter with continuous, integral indication of acceptable fluid seal fill level. The fluid seal trough shall be filled at the factory.
			2. Filter fluid seal must be comprised of a two component, slow-cured, polysiloxane elastomeric sealant and be self-leveling.
				1. Fluid seal material shall be characterized for all salient mechanical, physical, and chemical properties such as Hardness/Penetration, Tack, and Migration of free silicone (i.e. Blot Plot testing).
				2. Fluid seal material shall be characterized for chemical resistance to known industry accepted decontamination agents, cleaning agents, and filter testing reagents.
				3. Fluid seal material shall be tested for chemical compatibility to all materials in contact during manufacturing including gloves, tools, mixing equipment, dispensing equipment, and packaging materials, as well as potential airborne contaminants & poisons.
				4. Fluid seal material shall demonstrate resistance to accelerated life cycle testing.
				5. Fluid Seal shall withstand knife edge insertion to partial depth without complete depth cutting or full length splitting.
		6. Each filter shall have a unique label indicating filter size, lot number, unique serial number, model number, tested efficiency, pressure drop at volumetric test airflow, and UL compliance.
		7. Manufacturing shall take place in an ISO 7 cleanroom as determined by ISO 14644. Packaging shall be in a minimum ISO 6 cleanroom as determined by ISO 14644.
6. Shipping, Storage and Handling of HEPA/ULPA Filters
	1. Filter Assemblies are to be packaged discretely in sealed polyethylene bag and double wall corrugated carton of sufficient strength.
		1. Manufacturer shall characterize packaging against industry standards for:
			1. Drop
			2. Compression (i.e. stacking of cartons)
			3. Vibration
	2. The carton shall be labeled with the manufacturer’s part number, serial number, and test performance data.
	3. Palletized cartons shall be protected with corner posts and retained via stretch wrap.
	4. Filter Assemblies shall be shipped in fully enclosed trailers and in original, unopened packaging.
	5. Appropriate care must be exercised in handling cartons to avoid dropping, vibration, and rough handling to prevent potential for damage.
	6. HEPA Filter Assemblies shall be stored per manufacturer’s instructions for proper orientation, stacking configuration and limitations, and must remain in unopened cartons to prevent damage and exposure to potential contaminants.
	7. Cartons stored longer than one week shall remain unopened and in a climate controlled environment of 60-80F and 30-70%RH.
	8. Filter Assemblies shall remain in the sealed, unopened carton until inspection, testing and installation.
7. Filter Performance Criteria/Factory testing:
	1. Factory Efficiency and Resistance Test:
		1. The filter shall have a minimum overall efficiency of 99.99%-99.999% on 0.3 microns or 0.12 microns on filters 99.9995% and higher, Filter shall be tested and constructed in accordance with IEST-RP-CC001, latest version.
			1. The filter efficiency, as determined as the lower efficiency when tested for particle size ranges of 0.1-0.2 µm and 0.2-0.3 µm, shall be accomplished using a thermal condensation aerosol generator or Q107 Penetrometer and photometer which will measure gross downstream penetration as compared to the upstream concentration.
		2. Each Filter shall be tested for initial (clean) pressure drop at rated flow.

			1. All cleanroom style filters are tested at 90 FPM, +/- 10% and are based on filter media area. For example, an actual 24” x 24” filter has an area of 4 ft2, thus a tested flow rate of 400 CFM. The maximum initial pressure drop per overall efficiency rating is as follows:

|  |  |  |  |
| --- | --- | --- | --- |
| **Overall Efficiency** | **2” Max. initial ΔP** | **3” Max. initial ΔP** | **4” Max. initial ΔP** |
| 99.99% | 0.52 ”w.g.  | 0.45 “w.g. | 0.35 “w.g. |
| 99.9995% | 0.63 “w.g. | 0.50 “w.g. | 0.47 “w.g. |

* 1. Factory Scan Test:
		1. Filters with rated overall efficiency of 99.99% or higher shall be factory scanned in accordance with IEST-RP-CC034 latest version, to either 0.010% maximum penetration for a Type C/J, or 0.008% for a Type K over the entire filter face including glue lines and frame joints. The maximum useable face velocity shall be 125 FPM.
		2. The scanning shall be accomplished by passing the probe with overlapping strokes so the entire filter face area is sampled. Scanning shall be performed in accordance with IES-RP-CC034, latest revision section 6.2.2 “Discrete-particle counter filter scan test method”. A separate laser particle counter shall continuously monitor the upstream challenge concentration.
		3. The particle counting equipment shall have a detection limit of 0.10 micron or smaller at a sample flow rate of one (1) cubic foot per minute. The particle counting equipment should be calibrated and within its recommended calibration cycle.
		4. The challenge aerosol for factory scan testing is 4cST PAO (Poly Alpha Olefin). The two acceptable aerosol generation techniques are either the use of a laskin nozzle generator or an ATI, thermal condensation aerosol generator. The challenge aerosol concentration shall be a minimum of 1x108 particles per cubic foot.
		5. An acceptable alternative to the above method is a manual scan in accordance with IEST-RP-CC034.1 with the exception that the thermal condensation aerosol generator be utilized and the penetration limit is set to 0.008%. In this case the minimum aerosol concentration should be 10µg/L.
	2. Underwriters’ Laboratories (UL):
		1. Filter Assemblies shall be UL Standard 900 classified.
		2. Filter Assemblies shall be UL Standard 586 classified as required
	3. Labeling and Reporting:
		1. Each filter shall have a unique labeling indicating filter size, lot number, unique serial number, model number, tested efficiency, pressure drop at volumetric test airflow, and UL compliance.
		2. A test certificate shall be provided for each filter indicating filter specific test data including the lot and serial number along with the pressure drop and efficiency. A test certificate at a minimum should contain filter size, lot number, the filter’s unique serial number, model number, tested efficiency, tested pressure drop at volumetric test airflow, and scan test results. The challenge aerosol for both the efficiency and scan test must be outlined
		3. Each AstroHood S-II shall contain a label affixed to the unit with a stamped area ensuring pressure testing pass/fail criteria. Test reports should be provided.