- Acceptable Manufacturers

  - AAF Flanders

  - Other Approved Manufacturer

- Quality and Environmental Management Systems

  - The manufacturer shall have an ISO 9001 or ASME NQA-1 quality-based system at the manufacturing facility. The manufacturer shall make available documentation showing independent third-party certification or acceptable audit approvals and adherence to these systems.

  - If requested, manufacturer shall make available a copy of their Corporate Quality Manual.

- C3 HEPA Side Access Housing Construction

- Housing shall be constructed of 14-gauge galvanized or 304 stainless steel with 11-gauge corner posts for structural reinforcement.

- Joints are intermittently welded and are free of all burrs and sharp edges.  The joints are sealed airtight with silicone caulking.

- The access door shall have a ½” thick closed cell neoprene gasket around the inside perimeter.  Double pin hinges on the door shall pivot to enable the door to make level contact on the gasket when closed.  Stud bolts and stainless-steel wingnuts shall be used to secure the door.

- To accommodate duct connections, vertical flanges shall be 1-3/4” wide and horizontal flanges shall be 1-3/4” wide on the upstream side and 3” wide on the downstream side.

- The filter locking mechanism shall be a stainless-steel device with brass pivot block that presses the gasket seal filter against the sealing surface of the housing by means of a manually operated bolt and thrust assembly.  The assembly shall be operated with a standard ¾” socket or wrench.

- The prefilter tracks shall be fabricated from the same material as the housing.

- Options: Weathercap, pressure gages, static ports, aerosol test ports and insulated housings are available.