Middle Atlantic Products, Inc.	January 209

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 16

EQUIPMENT ENCLOSURES

Specifier Notes:  This section covers Middle Atlantic Products, Inc. WMRK Series Configured Enclosure.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Equipment enclosures.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	EIA/TIA 310D – Cabinets, Racks, Panels and Associated Equipment.

B.	ISO 9001:2000 – Quality Management Systems – Requirements.

C.	NFPA 70 – National Electrical Code (NEC).

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data, including options and accessories.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

- Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

- Conform to ISO 14025 and EN 15804 or ISO 21930 in the development of life cycle assessments (LCA) and Type III environmental product declarations (EPD).

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  Product lifetime.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	EQUIPMENT ENCLOSURES

A.	Equipment Enclosures:  WMRK Series Configured Enclosure.

Specifier Notes:  Specify equipment rack model number.  Consult Middle Atlantic Products product information for available models.

1.	Model:  WMRK-__________ .

2.	Type:  19-inch gangable equipment rack.

3.	Compliance:

a.	EIA/TIA 310D.

Specifier Notes:  Specify overall and useable dimensions.

5.	Overall Dimensions:

a.	Height:  _____ inches (_____ mm).

b.	Width:  24 inches (610 mm).

c.	Depth:  _____ inches (_____ mm).

6.	Useable Dimensions:

a.	Height:  _____ rackspaces.

b.	Depth:  _____ inches (_____ mm).

7.	Construction:  Fully welded.

8.	Weight Capacity:  1,000 pounds.

9.	Materials:

a.	Top and Bottom:  14-gauge steel.

b.	Horizontal Braces:  16-gauge steel.

c.	Rear Door:  18-gauge steel.

10.	Finish of Structural Elements:  Black textured powder coat.

11.	Rackrail:

a.	Two pairs of fully adjustable, 14-gauge steel rackrail with cage nut mounting holes in universal EIA spacing, includes two rear Z-rail adaptors.

b.	Finish:  Black powder coat.

c.	Rackspaces:  Numbered.

12.	Rear Door:  Split cupboard style, vented perforation with 76% open area.

13.	Removable Split Rear Knockout Panels:

a.	1/2-inch, 3/4-inch, 1-inch, and 1-1/2-inch electrical knockouts installed in bottom.

14.	Top Knockouts:

a.	1/2-inch, 3/4-inch, 1-inch, and 1-1/2-inch electrical knockouts and 5/8-inch BNC knockouts for UHF/VHF antennae formed in top.

- Grounding and Bonding Stud:  1/4-20 by 1-inch threaded, installed in base, allows installation to conform to NEC.

- Removable Bottom Rear Cable Entry Plate.

- Cable Gland Grommets: 4-inch diameter, quantity five, located in top.

- Cable Ladder Mounting Holes: top accepts 6-inch, 12-inch and 18-inch wide cable ladders.

- Temperature Monitor with Display: includes temperature probe with 9-foot wire, LED display, top front of rack.

- Vertical Lacer Strip: 3-1/4-inch width, highly perforated, cable tie posts.

- Vertical Power Strip: 20 Amp, 10 outlet, corded.

- Mounting Hardware: 100.

2.3	OPTIONS

Specifier Notes:  Specify required options.  Delete options not required.  Consult Middle Atlantic Products for more information.

A.	Cable Ladder: 12-inch wide, [6-foot long] [10-foot long].

B.	Lacer Strip: 11-gauge steel, highly perforated.

C.	Horizontal Lacer Bars.

D.	Horizontal Cable Managers.

E.	Ganging Hardware.

F.	Wrinkle touch-up paint.

G.	Copper buss bar.

H.	Door latch.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive equipment enclosures.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install equipment enclosures in accordance with manufacturer’s instructions at locations indicated on the Drawings.

B.	Install equipment enclosures plumb, level, and square.

3.3	ADJUSTING

A.	Adjust operating hardware to operate smoothly without binding.

B.	Repair minor damages to finish in accordance with manufacturer’s instructions and as approved by Architect.

3.4	PROTECTION

A.	Protect installed equipment enclosures from damage during construction.

END OF SECTION