Middle Atlantic Products, Inc.	August 2015

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 23

CABLE LADDERS

Specifier Notes:  This section covers Middle Atlantic Products, Inc. CL Series Cable Ladders.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Cable ladders.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	EIA/TIA 310D – Cabinets, Racks, Panels and Associated Equipment.

B.	ISO 9001:2000 – Quality Management Systems – Requirements.

C.	UL – Underwriters Laboratories.

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data, including accessories.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

A.	Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials and finish during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  Product lifetime.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	CABLE LADDERS

A.	Single-Piece, Straight Cable Ladder Sections:  CL Series Cable Ladders.

Specifier Notes:  Specify cable ladder model number.

1.	Model:  [CLB-10]  [CLB-6].

2.	Compliance:  EIA/TIA 310D.

3.	UL Classified:  US and Canada.

4.	Ladder Section Dimensions:

Specifier Notes:  Specify ladder section length.

a.	Length:  [71 inches]  [119 inches].

b.	Width:  12 inches.

c.	Thickness:  1.5 inches.

5.	Rungs:

a.	Dimensions:  1 inch by 0.5 inch by 11.25 inches.

Specifier Notes:  Specify number of rungs per section based on ladder section length.

b.	Ladder Section:  [8]  [13] rungs on 9-inch centers.

6.	Construction:  Fully welded.

7.	Weight Capacity:  187 pounds per foot, based on 4-foot support span.

8.	Material:  Structural steel.

a.	Rungs:  11-gauge.

b.	Ladders:  16-gauge.

9.	Finish:  Two layers, black powder coat.

B.	90-Degree, Horizontal-Bend Cable Ladder Sections:  CL Series Cable Ladders.

1.	Model:  CLB-90HB.

2.	Compliance:  EIA/TIA 310D.

3.	UL Classified:  US and Canada.

4.	Ladder Section Dimensions:

a.	Width:  12 inches.

b.	Length:  27 inches.

c.	Thickness:  1.5 inches.

5.	Rungs:

a.	Dimensions:  1 inch by 0.5 inch by 11.25 inches.

b.	Ladder Section:  4 rungs on 5.2-inch centers on inside of bend and 10.25-inch centers on outside of bend.

6.	Construction:  Fully welded.

7.	Weight Capacity:  187 pounds per foot, based on 4-foot support span.

8.	Material:  Structural steel.

a.	Rungs:  11-gauge.

b.	Ladders:  16-gauge.

9.	Finish:  Two layers, black powder coat.

C.	90-Degree, Vertical-Inside-Bend Cable Ladder Sections:  CL Series Cable Ladders.

1.	Model:  CLB-VI90.

2.	Compliance:  EIA/TIA 310D.

3.	UL Classified:  US and Canada.

4.	Ladder Section Dimensions:

a.	Width:  12 inches.

b.	Length:  15.5 inches.

c.	Thickness:  1.5 inches.

5.	Rungs:

a.	Dimensions:  1 inch by 0.5 inch by 11.25 inches.

b.	Ladder Section:  4 rungs on 4.8-inch centers.

6.	Construction:  Fully welded.

7.	Weight Capacity:  187 pounds per foot, based on 4-foot support span.

8.	Material:  Structural steel.

a.	Rungs:  11-gauge.

b.	Ladders:  16-gauge.

9.	Finish:  Two layers, black powder coat.

D.	90-Degree, Vertical-Outside-Bend Cable Ladder Sections:  CL Series Cable Ladders.

1.	Model:  CLB-VO90.

2.	Compliance:  EIA/TIA 310D.

3.	UL Classified:  US and Canada.

4.	Ladder Section Dimensions:

a.	Width:  12 inches.

b.	Length:  15.5 inches.

c.	Thickness:  1.5 inches.

5.	Rungs:

a.	Dimensions:  1 inch by 0.5 inch by 11.25 inches.

b.	Ladder Section:  4 rungs on 5.3-inch centers.

6.	Construction:  Fully welded.

7.	Weight Capacity:  187 pounds per foot, based on 4-foot support span.

8.	Material:  Structural steel.

a.	Rungs:  11-gauge.

b.	Ladders:  16-gauge.

9.	Finish:  Two layers, black powder coat.

2.3	ACCESSORIES

Specifier Notes:  Specify required accessories.  Delete accessories not required.  Consult Middle Atlantic Products for more information.

A.	Adjustable Horizontal Splice Hardware:

1.	UL Classified:  US and Canada.

2.	Material:  Steel with zinc coating.

3.	Pair.

B.	Ladder End Splice Hardware:

1.	UL Classified:  US and Canada.

2.	Material:  Steel with zinc coating.

3.	Pair.

C.	90-Degree Horizontal Tee-Splice Hardware:

1.	UL Classified:  US and Canada.

2.	Material:  Steel with zinc coating.

3.	Pair.

D.	Adjustable Ladder End Splice Hardware:

1.	UL Classified:  US and Canada.

2.	Material:  Steel with zinc coating.

3.	Pair.

E.	Adjustable 90-Degree Tee-Splice Hardware:

1.	UL Classified:  US and Canada.

2.	Material:  Steel with zinc coating.

3.	Pair.

F.	Triangle Wall Support Brackets:

1.	Material:  Steel with black powder coat finish.

G.	Cable Ladder End Drop with 3 Cable Spools:

1.	UL Classified:  US and Canada.

2.	End Drop:  Aluminum with black powder coat finish.

3.	Cable Spools:  Black plastic.

H.	Cable Ladder Side Drop with 3 Cable Spools:

1.	UL Classified:  US and Canada.

2.	Side Drop:  Aluminum with black powder coat finish.

3.	Cable Spools:  Black plastic.

I.	Ladder Wall Clamps:

1.	Material:  Steel with zinc coating.

2.	Pair.

J.	Ladder Wall Supports:

1.	Material:  Steel with black powder coat finish.

K.	Ladder Center Support Brackets:

1.	Material:  Steel with black powder coat finish.

L.	Slotted Ladder Support Hardware with Ceiling Hang Kit:

1.	Material:  Steel with zinc coating.

2.	Pair.

M.	Ladder End Support Hardware:

1.	Material:  Steel with zinc coating.

2.	Pair.

N.	Plastic Cable Spools:

1.	Material:  Black plastic.

2.	Quantity:  10.

O.	Ladder End Caps:

1.	Material:  Black rubber.

2.	Six pairs.

P.	Cable Ladder Bonding Kit:

1.	UL Classified:  US and Canada.

2.	J-Bolts:  Pair.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive cable ladders.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install cable ladders in accordance with manufacturer’s instructions at locations indicated on the Drawings.

B.	Install cable ladders plumb, level, square, and secure.

3.3	ADJUSTING

A.	Repair minor damages to finish in accordance with manufacturer’s instructions and as approved by Architect.

3.4	PROTECTION

A.	Protect installed cable ladders from damage during construction.

END OF SECTION