Middle Atlantic Products, Inc.	January 2019

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 16

CABLE MANAGEMENT ENCLOSURES

Specifier Notes:  This section covers Middle Atlantic Products, Inc. DRK Series 19-Inch Panel Width Cable Management Enclosure.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	19-inch panel width cable management enclosures.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

B.	CBC – California Building Code.

C.	EIA/TIA 310D – Cabinets, Racks, Panels and Associated Equipment.

D.	IBC – International Building Code.

E.	ISO 9001:2000 – Quality Management Systems – Requirements.

F.	NFPA 5000 – Building Construction and Safety Code.

G.	UBC – Uniform Building Code.

H.	UL – Underwriters Laboratories.

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data, including options.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

- Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

- Conform to ISO 14025 and EN 15804 or ISO 21930 in the development of life cycle assessments (LCA) and Type III environmental product declarations (EPD).

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials and finish during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  Product lifetime.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	CABLE MANAGEMENT ENCLOSURES

A.	Cable Management Enclosures:  DRK Series 19-Inch Panel Width Cable Management Enclosure.

Specifier Notes:  Specify cable management enclosure model number.  Consult Middle Atlantic Products product information for available models.

1.	Model:  DRK19-44-__________ .

2.	Type:  19-inch panel width, gangable, equipment enclosure.

3.	Compliance:

a.	EIA/TIA 310D.

b.	Seismic Certified:  Seismic certified to 1997 UBC and 2001 CBC Seismic Zone 4 and 2000 IBC, 2003 IBC, 2002 ASCE Standard 7, and 2003 NFPA 5000 Seismic Use Group III lateral force requirements for protecting 750 pounds of essential equipment in upper floor installations when used with optional MRK-Z4 seismic floor anchor brackets with Ip value of 1.5.

4.	UL Listed:  US and Canada.

5.	Overall Dimensions:

a.	Height:  83-1/2 inches (2,121 mm).

b.	Width:  30 inches (762 mm).

Specifier Notes:  Specify overall depth.

c.	Depth:  _____ inches ( _____ mm).

6.	Useable Dimensions:

a.	Useable Height:  44 rackspaces.

Specifier Notes:  Specify useable depth.

b.	Useable Depth:  _____ inches ( _____ mm).

7.	Construction:  Fully welded.

8.	Weight Capacity:  2,500 pounds.

9.	Materials:

a.	Top and Bottom:  14-gauge steel.

b.	Horizontal Braces:  1/8-inch thick structural steel.

10.	Finish of Structural Elements:  Black textured powder coat.

11.	Ventilation:  10-inch fan top with fan guard.

12.	Integral Cable Management Ducts:  Pair of cable ducts with solid steel hinged doors and 4-point magnetic closure pre-installed in front.

13.	Rackrail:

a.	Two pairs.

b.	11-gauge steel with [tapped 10-32]  [6-mm cage nut] mounting holes in universal EIA spacing.

c.	Finish:  Black e-coat.

d.	Rackspaces:  Numbered.

14.	Rear Door:  Vented.

15.	Removable Rear Knockout Panels, Top and Bottom:  1/2-inch, 3/4-inch, 1-inch, and 1-1/2-inch electrical knockouts.

16.	Grounding and Bonding Studs:  Zinc plated, 1/4-20 by 1-inch threaded, installed 2 in base and 2 in top.

17.	Rack Screws:  100.

2.3	OPTIONS

Specifier Notes:  Specify required options.  Delete options not required.  Consult Middle Atlantic Products for more information.

A.	Front Doors:  [Vented plexi]  [Plexi]  [Vented].

B.	Rear Doors:  [Fully vented]  [Partially vented]  [Fully perforated].

C.	Side Panels:  Keylocked, pair.

D.	Additional Rail Kit:  11-gauge steel, 10-32 threaded, with EIA numbered spacing.

E.	Additional Rail Kit:  11-gauge steel, cage-nut style, with EIA numbered spacing.

F.	Integrated Fan Tops:

1.	Proportional-speed thermostatic fan control.

2.	[Four 4-1/2-inch quiet fans]  [10-inch fan].

G.	Tops:  [Solid]  [Vented, perforated]  [Vented, slot pattern]  [Mounts on 10-inch fan]  [Mounts four 4.5-inch fans]  [Accepts 6-inch and 12-inch cable ladders]  [2-space brush grommet]  [13-space rackrail].

H.	Caster Base:

1.	Overall Depth:  [31-1/2 inches]  [36 inches].

I.	Keylocked Side Panels:

1.	Removable, pair.

2.	Overall Depth:  [31-1/2 inches]  [36 inches]  [42 inches].

J.	Additional cable duct.

K.	Rail Bracket Adaptors:  Allow for mounting of blank or other panels vertically between rackrail brackets.

L.	Seismic compliancy floor anchor brackets.

M.	Copper buss bar.

N.	Document pocket.

O.	Door latch.

P.	Ganging hardware.

Q.	Leveling feet.

R.	Wrinkle touch-up paint.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive cable management enclosures.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install cable management enclosures in accordance with manufacturer’s instructions at locations indicated on the Drawings.

B.	Install cable management enclosures plumb, level, square, and secure.

3.3	ADJUSTING

A.	Adjust operating hardware to operate smoothly without binding.

B.	Repair minor damages to finish in accordance with manufacturer’s instructions and as approved by Architect.

3.4	PROTECTION

A.	Protect installed cable management enclosures from damage during construction.

END OF SECTION