Middle Atlantic Products, Inc.	January 2019

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 16

WALL-MOUNT PIVOTING EQUIPMENT RACKS

Specifier Notes:  This section covers Middle Atlantic Products, Inc. DWR Series Wall-Mount Rack.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Wall-mount pivoting equipment racks.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	EIA/TIA 310D – Cabinets, Racks, Panels and Associated Equipment.

B.	ISO 9001:2000 – Quality Management Systems – Requirements.

C.	UL – Underwriters Laboratories.

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data, including options.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

- Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

- Conform to ISO 14025 and EN 15804 or ISO 21930 in the development of life cycle assessments (LCA) and Type III environmental product declarations (EPD).

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials and finish during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  Product lifetime.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	WALL-MOUNT PIVOTING EQUIPMENT RACKS

A.	Wall-Mount Pivoting Equipment Racks:  DWR Series Wall-Mount Rack.

Specifier Notes:  Specify wall-mount equipment rack model number.  Consult Middle Atlantic Products product information for available models.

1.	Model:  DWR-__________ .

2.	Type:  19-inch wall-mount rack.

3.	Compliance:  EIA/TIA 310D.

4.	UL Listed:  US and Canada.

Specifier Notes:  Specify overall and useable dimensions.

5.	Overall Dimensions:

a.	Overall Width:  23.40 inches (594 mm).

b.	Overall Height:  _____ inches ( _____ mm).

c.	Overall Depth:  _____ inches ( _____ mm).

6.	Useable Dimensions:

a.	Useable Racking Height:  _____ inches ( _____ mm).

b.	Useable Depth:  _____ inches ( _____ mm), extends into backpan 3.5 inches.

Specifier Notes:  Specify number of rackspaces.

7.	Rackspaces:  _____ .

Specifier Notes:  Specify weight capacity.

8.	Weight Capacity:  _____ pounds.

9.	Mounting:  Tool-free “Quick-Mount” system for one-person mounting of center section to backpan at site.

10.	Center Section and Backpan:

a.	16-gauge steel.

Specifier Notes:  Specify finish color.

b.	Finish:  [Black-textured]  [Granite gray-textured] powder coat.

11.	Corner Braces:  1/8-inch thick.

12.	Rackrail:

a.	11-gauge steel with tapped 10-32 mounting holes in universal EIA spacing.

b.	Finish:  Black e-coat.

c.	Rackspaces:  Marked.

13.	Backpan:  Raised mounting embosses to mount power products and other accessories.

14.	Rack:  Swing open for component cabling access.

a.	Center Section:  Pivot for left or right opening.

15.	Raceways:  Wiremold 4000 Series.

16.	Knockouts:

a.	Center Section:

1)	Decora Knockouts:  Top and bottom of face.

2)	Fan Knockouts:  Top and bottom, each accepts up to two 4-1/2-inch fans.

b.	Backpan:

1)	Electrical Knockouts:  Top and bottom, 3/4 inch, 1 inch, 1-1/2 inches, 2 inches, and 3 inches.

2)	BNC Knockouts:  Top and bottom, 5/8-inch UHF/VHF antenna knockouts.

3)	Laser Knockout:  Backpan, 12-1/2-inch by 12-inch opening for through-wall cable pass-through.

4)	UCP Knockouts:  Locking side of backpan accepts 1 UCP panel.

17.	Top, Bottom, and Sides:  Vertical vent pattern, center section.

18.	Lacing Points:  Throughout interior to facilitate cable management.

19.	Latch:  Pad lockable.

20.	Keylock:  Standard 1/4 turn.

21.	Grounding and Bonding Studs:  1/4-20 by 1-inch threaded, installed in center section and backpan.

2.3	OPTIONS

Specifier Notes:  Specify required options.  Delete options not required.  Consult Middle Atlantic Products for more information.

A.	Front Door:  Reinforced 16-gauge steel, [solid]  [vented, 22 percent open area]  [vented, 63 percent open area]  [plexi].

1.	Hinges:  Zinc die cast, can be installed while rack is fully loaded with equipment.

B.	Keyless Latch:  Replaces keylock, fits front and rear doors.

C.	Rear Rail Kit:  11-gauge steel, 10-32 threaded, pair, includes hardware.

D.	Vent Blockers:  Promotes active thermal management.

E.	Zero-Clearance Latch:  Allows close proximity mounting.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive wall-mount pivoting equipment racks.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install wall-mount pivoting equipment racks in accordance with manufacturer’s instructions at locations indicated on the Drawings.

B.	Install wall-mount pivoting equipment racks plumb, level, square, and secure.

Specifier Notes:  Specify left-hand or right-hand swing.

C.	Mount racks for [left-hand]  [right-hand] swing.

3.3	ADJUSTING

A.	Adjust operating hardware to operate smoothly without binding.

B.	Repair minor damages to finish in accordance with manufacturer’s instructions and as approved by Architect.

3.4	PROTECTION

A.	Protect installed wall-mount pivoting equipment racks from damage during construction.

END OF SECTION