Middle Atlantic Products, Inc.	October 2006

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 26

COMMUNICATIONS RACKS – MOUNTED POWER STRIPS

Specifier Notes:  This section covers Middle Atlantic Products, Inc. PDT Series Thin Power Strips for installation in equipment racks.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Thin power strips for installation in equipment racks.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	ISO 9001:2000 – Quality Management Systems – Requirements.

B.	NFPA 70 – National Electrical Code (NEC).

Specifier Notes:  Include UL 5 when specifying power strips with J-box.  Include UL 1363 when specifying power strips with cord.

C.	[UL 5 – Standard for Surface Metal Raceways and Fittings]  [UL 1363 – Standard for Relocatable Power Taps].

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

A.	Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  3 years.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	POWER STRIPS

A.	High-Density Thin Power Distribution Strips:  PDT Series thin power strips.

Specifier Notes:  Specify power strip model number.  Consult Middle Atlantic Products product information for available models.

1.	Model:  PDT-_______________ .

2.	Compliance:  NEC.

3.	UL Listed:  US and Canada.

Specifier Notes:  Include UL 5 when specifying power strips with J-box.  Include UL 1363 when specifying power strips with cord.

a.	[UL 5]  [UL 1363].

4.	Outlets:

Specifier Notes:  Specify number and type of outlets.

a.	Number:  [20]  [10].

b.	Type:  [NEMA 5-15R]  [NEMA 5-20R].

Specifier Notes:  Specify circuit Amps.

5.	Circuit:  [15 Amps]  [20 Amps].

6.	Overall Dimensions:

Specifier Notes:  Specify overall length.  20-outlet models are 72-3/4 inches long.  10-outlet models are 37-3/4 inches long.

a.	Chassis Length:  [72-3/4 inches (1,848 mm)]  [37-3/4 inches (959 mm)].

b.	Depth:  1 inch (25 mm).

Specifier Notes:  Specify overall width.  20-Amp models are 1.9 inches wide.  15-Amp models are 1.3 inches wide.

c.	Width:  [1.9 inches (48 mm)]  [1.3 inches (33 mm)].

7.	J-Box Dimensions:

a.	Depth:  2 inches (51 mm).

Specifier Notes:  Specify width of J-box.  20-Amp models are 2 inches wide.  15-Amp models are 1.5 inches wide.

b.	Width:  [2 inches (51 mm)]  [1.5 inches (38 mm)].

8.	Corded Models:

a.	Terminated with 10-foot power cord.

Specifier Notes:  Specify plug.  15-Amp models use NEMA 5-15P plug.  20-Amp models use NEMA 5-20P or L5-20P plug.

b.	Plug:  NEMA [5-15P]  [5-20P]  [L5-20P].

9.	Regular and Top Feed Models:  Accommodate installations where ground prongs are positioned at top of each outlet.

10.	Power Strips with J-Box:

a.	Field configurable single or dual circuits in both 15-Amp and 20-Amp models.

b.	Field configurable isolated ground models.

11.	Factory assembled.

12.	Chassis:  Aluminum.

13.	Finish:  Black anodized.

14.	Mounting:  Included.

2.3	ACCESSORIES

A.	Cable management clips.

B.	Mounting clips.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine equipment racks to receive power strips.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install power strips in equipment racks in accordance with manufacturer’s instructions at locations indicated on the Drawings.

3.3	PROTECTION

A.	Protect installed power strips from damage during construction.

END OF SECTION