Middle Atlantic Products, Inc.	August 2006

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 16

OPEN-FRAME EQUIPMENT RACKS

Specifier Notes:  This section covers Middle Atlantic Products, Inc. RL Series Open-Frame Rack.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Open-frame equipment racks.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	EIA/TIA 310D – Cabinets, Racks, Panels and Associated Equipment.

B.	ISO 9001:2000 – Quality Management Systems – Requirements.

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data, including options.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

A.	Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials and finish during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  Product lifetime.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	OPEN-FRAME EQUIPMENT RACKS

A.	Open-Frame Equipment Racks:  RL Series Open-Frame Rack.

Specifier Notes:  Specify open-frame equipment rack model number.  Consult Middle Atlantic Products product information for available models.

1.	Model:  RL-__________ .

2.	Type:  19-inch open-frame equipment rack.

3.	Compliance:  EIA/TIA 310D.

Specifier Notes:  Specify overall and useable height.

4.	Overall Dimensions:

a.	Height:  _____ inches ( _____ mm).

b.	Width:  19.62 inches (498 mm).

c.	Depth:  15.25 inches (387 mm).

5.	Useable Height:  _____ rackspaces.

6.	Assembly:  Field assembly, self-aligning design.

7.	Weight Capacity:

a.	Weight Evenly Distributed with Base Securely Fastened:  800 pounds.

b.	Weight Evenly Distributed with Base Securely Fastened and Top Braced to Structural Building Component:  1,600 pounds.

Specifier Notes:  Specify thread type.

8.	Relay Channels: 11-gauge steel with tapped _____ mounting holes in universal EIA spacing.

9.	Top Angles:  0.125-inch thick aluminum.

10.	Gusseted Foot Base:  Taper on feet to allow rack to self-stabilize on uneven floors.

11.	Rack Screws:  50.

12.	Finish:  Black powder coat.

2.3	OPTIONS

Specifier Notes:  Specify required options.  Delete options not required.  Consult Middle Atlantic Products for more information.

A.	Cantilever support base.

B.	Center cable organizer.

C.	End cable organizer.

D.	Cable organizer covers.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive open-frame equipment racks.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install open-frame equipment racks in accordance with manufacturer’s instructions at locations indicated on the Drawings.

B.	Install open-frame equipment racks plumb, level, square, and secure.

C.	Drill top angles for cable ladder installation as required.

3.3	ADJUSTING

A.	Repair minor damages to finish in accordance with manufacturer’s instructions and as approved by Architect.

3.4	PROTECTION

A.	Protect installed open-frame equipment racks from damage during construction.

END OF SECTION