Middle Atlantic Products, Inc.	August 2006

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 16

ALUMINUM OPEN-FRAME EQUIPMENT RACKS

Specifier Notes:  This section covers Middle Atlantic Products, Inc. RLA Series Aluminum Open-Frame Rack.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Aluminum open-frame equipment racks.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	EIA/TIA 310D – Cabinets, Racks, Panels and Associated Equipment.

B.	ISO 9001:2000 – Quality Management Systems – Requirements.

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data, including options.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

A.	Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials and finish during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  Product lifetime.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	ALUMINUM OPEN-FRAME EQUIPMENT RACKS

A.	Aluminum Open-Frame Equipment Racks:  RLA Series Aluminum Open-Frame Rack.

Specifier Notes:  Specify aluminum open-frame equipment rack model number and other data.  Consult Middle Atlantic Products product information for available models.

1.	Model:  RLA__________ .

2.	Type:  [19-inch]  [23-inch] open-frame equipment rack.

3.	Compliance:  EIA/TIA 310D.

4.	Overall Dimensions:

a.	Height:  83-3/4 inches (2,127 mm).

b.	Width:  [20.25 inches (514 mm)]  [24.25 inches (616 mm)].

c.	Depth:

1)	Top:  6 inches (152 mm).

2)	Base:  15 inches (381 mm).

Specifier Notes:  Specify panel width.

5.	Panel Width:  [19 inches]  [23 inches].

6.	Rack Units of Vertical Space:  45.

7.	Construction:  Knock down.

8.	Weight Capacity:  1,600 pounds.

9.	Vertical Channels:

a.	Quantity:  Two.

b.	Material:  Extruded aluminum.

c.	Size:  3-1/4 inches wide by 3/16 inch thick.

d.	Mounting Holes:  Tapped 12-24 front and rear on EIA mounting centers.

10.	Top Angle:  Extruded aluminum, 3/16 inch thick.

11.	Base:  Extruded aluminum, 1/4 inch thick.

Specifier Notes:  Specify finish.

12.	Finish:  [Silver brushed aluminum]  [Black powder coat].

13.	Rack Screws:  Twenty-five 12-24 tapped.

B.	Cable Carrier:

1.	Model:  RLA-CC.

2.	Overall Dimensions:

a.	Height:  82.7 inches (2,101 mm).

b.	Width:  5 inches (127 mm).

c.	Depth:  6 inches (152 mm).

3.	Material:  16-gauge steel.

4.	Hinged Door:  Steel, solid, with 3-point magnetic catch.

5.	Cable Management:

a.	Sides and Rear:  Fifty-three 3-inch high by 2.25-inch wide cable pass-through points.

b.	Raised Bridge Lances for Cable Lacing:  36.

2.3	OPTIONS

Specifier Notes:  Specify required options.  Delete options not required.  Consult Middle Atlantic Products for more information.

A.	Horizontal cable managers.

B.	Horizontal lacer bars.

C.	Rackmount Cable Tray:  [1 rackspace]  [2 rackspaces].

D.	Vented center mount shelf.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive aluminum open-frame equipment racks.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install aluminum open-frame equipment racks in accordance with manufacturer’s instructions at locations indicated on the Drawings.

B.	Install aluminum open-frame equipment racks plumb, level, square, and secure.

3.3	ADJUSTING

A.	Repair minor damages to finish in accordance with manufacturer’s instructions and as approved by Architect.

3.4	PROTECTION

A.	Protect installed aluminum open-frame equipment racks from damage during construction.

END OF SECTION