Specification Table

| Description |  | RLNK-P415 | RLNK-P420 |
| --- | --- | --- | --- |
| Input Voltage | 80-140VAC 60/50Hz |  |  |
| Full Load Input Current at V AC |  | 120VAC 15A | 120VAC 20A |
| # of Outlets |  | 4 | 4 |
| Output Voltage Range |  | FIXED +/- 5% | FIXED +/- 5% |
| Output MAX Current |  | 15A | 20A |
| Output Contentious Current |  | 12A | 16A |
| No Load Power Dissipation |  | < 1W | < 1W |
| Connection Type |  | 9ft. 15A IEC power cord | 9ft. 20A IEC power cord |

Hardware Features

| Surge Protection | Two-Stage MOV | Two-Stage MOV |
| --- | --- | --- |
| Peak Impulse Current (8/20uS waveform) | 30,000 Amps, one time - Maximum peak impulse current pulse as defined between line and neutral 19,500 Amps, two times within 5 minutes - Maximum multiple impulse current derated per spec |  |
| Protection Mode | Line to Neutral only; no ground contamination |  |
| Response Time | Less than 1 nanosecond |  |
| Surge Enginery Dissipation | 711 Joules (10 / 100 micro seconds) |  |
| EMI/RF Suppression | >20dB Calculated Line to Neutral - 100kHz to 1Mhz - based on nominal impedance |  |
| Voltage Protection Rating | N/A | N/A |
| Clamping Voltage | N/A | N/A |
| UL 1449 ADJUNCT | N/A | N/A |
| Classification Test Results |  |  |
| EMI Filter, Differential Mode | N/A | N/A |
| 50-OHM Load | N/A | N/A |
| EMI Filter, Common Mode | N/A | N/A |
| 50-OHM Load | N/A | N/A |
| Maximum Applied Surge Voltage | N/A | N/A |
| Maximum Applied Surge Current | N/A | N/A |
| Maximum Applied Surge Energy | N/A | N/A |
| Endurance | N/A | N/A |
| External Sensors connection | Up to 32 external sensors |  |
| Wi-Fi Capable | USB WiFi dongle |  |

Software Features

| Communication | SNMP, SSL/TLS/SSH,SMTP,NTP,DDNS,Cloud,CLI TCIP/IP/USB RS-232, HTTPS, HTTP,HyperTerminal, Telnet |
| --- | --- |
| Discovery | Racklink Discover Tool |
| LCD display | Yes |
| Network Security | Yes/Certificates |
| Control Functions | 4 individual controllable outlets |
| Data Monitoring | Data Logging/Metering |
| Supported Web Browser | Internet Explorer 11, Windows Edge, Firefox 25 and later, Safari(MAC) Google Chrome, Android, and iOS |
| Network Server Status | AutoPing monitoring |

General

| Certifications | UL 60950-1 and CSA C22.2 No.60950-1, FCC Part 15, Class B |
| --- | --- |
| Dimensions (WxHxD) | 14.00x9.75x4.75 |
| Weight | 6.6lbs |

Warranty

| Power Products | Standard Rack Mount or Vertical Power 3 years |
| --- | --- |
|  | Series Protection 12 years |

For complete warranty information, refer to http://www.middleatlantic.com/company/about-us.aspx#warranty