Middle Atlantic Products, Inc.	January 2019

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 16

EQUIPMENT ENCLOSURES

Specifier Notes:  This section covers Middle Atlantic Products, Inc. VRK Series Enclosure.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Equipment enclosures.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

B.	CBC – California Building Code.

C.	EIA/TIA 310D – Cabinets, Racks, Panels and Associated Equipment.

D.	IBC – International Building Code.

E.	ISO 9001:2000 – Quality Management Systems – Requirements.

F.	NFPA 5000 – Building Construction and Safety Code.

G.	UBC – Uniform Building Code.

H.	UL – Underwriters Laboratories.

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data, including options.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

- Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

- Conform to ISO 14025 and EN 15804 or ISO 21930 in the development of life cycle assessments (LCA) and Type III environmental product declarations (EPD).

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials and finish during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  Product lifetime.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	EQUIPMENT ENCLOSURES

A.	Equipment Enclosures:  VRK Series Enclosure.

Specifier Notes:  Specify equipment enclosure model number.  Consult Middle Atlantic Products product information for available models.

1.	Model:  VRK-__________ .

2.	Type:  19-inch, gangable equipment enclosure.

3.	Compliance:

a.	EIA/TIA 310D.

b.	Seismic Certified:  Seismic certified to 1997 UBC and 2001 CBC Seismic Zone 4 and 2000 IBC, 2003 IBC, 2002 ASCE Standard 7, and 2003 NFPA 5000 Seismic Use Group III lateral force requirements for protecting 775 pounds of essential equipment in upper floor installations when used with optional VRK-Z4 seismic floor anchor brackets with Ip value of 1.5.

4.	UL Listed:  US and Canada.

Specifier Notes:  Specify overall and useable dimensions.

5.	Overall Dimensions:

a.	Height:  83-1/8 inches (2,111 mm).

b.	Width:  22 inches (558 mm).

c.	Depth:  _____ inches ( _____ mm).

6.	Useable Dimensions:

a.	Height:  44 rackspaces.

b.	Depth:  _____ inches ( _____ mm).

7.	Construction:  Fully welded.

8.	Weight Capacity:  2,500 pounds.

9.	Materials:

a.	Top and Bottom:  14-gauge steel.

b.	Horizontal Braces:  16-gauge steel, welded to uprights of 16-gauge steel, giving 1/8-inch thick structure.

c.	Rear Door:  18-gauge steel.

10.	Finish of Structural Elements:  Black textured powder coat.

11.	Rackrail:

a.	Two pairs, fully adjustable, 11-gauge steel rackrail with tapped 10-32 mounting holes in universal EIA spacing.

b.	Finish:  Black e-coat.

c.	Rackspaces:  Numbered and bracketed.

12.	Top and Bottom Face:  Vertical slotted vent pattern.

13.	Sides:  Sixteen 1/2-inch thick, pre-installed, horizontal lacing bars.

14.	Grounding and Bonding Studs:  1/4-20 by 1-inch threaded, installed in base.

2.3	OPTIONS

Specifier Notes:  Specify required options.  Delete options not required.  Consult Middle Atlantic Products for more information.

A.	Front Doors:  Reinforced 16-gauge steel, [solid]  [vented, 22 percent open area]  [vented, 63 percent open area]  [plexi]  [vented plexi].

B.	Vented Rear Door:  steel, [vented, top and bottom]  [large perf, 63 percent open area].

C.	Removable Keylocked Side Panels:  Keylocked with recessed lift handles.

D.	Top Panels:  16-gauge steel, [solid]  [accepts 10-inch fan]  [accepts up to four 4-1/2-inch fans]  [vented]  [accepts 6-inch and 12-inch wide cable ladders]  [pagoda vented, adds 1.41 inches to top of enclosure]  [10-inch fan with integrated fan control]  [four 4-1/2-inch quiet fans with integrated fan control].

E.	Keyless Latch:  Replaces keylock, front and rear doors.

F.	Lacer Strip:  11-gauge steel, heavily perforated, 77 inches long.

G.	Additional Rail Kit:  11-gauge steel, 10-32 threaded, pair, includes hardware.

H.	Seismic compliancy floor anchor brackets.

I.	Copper buss bar.

J.	Document pocket.

K.	Ganging hardware.

L.	Top rails.

M.	Universal front doors.

N.	Wrinkle touch-up paint.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive equipment enclosures.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install equipment enclosures in accordance with manufacturer’s instructions at locations indicated on the Drawings.

B.	Install equipment enclosures plumb, level, square, and secure.

3.3	ADJUSTING

A.	Adjust operating hardware to operate smoothly without binding.

B.	Repair minor damages to finish in accordance with manufacturer’s instructions and as approved by Architect.

3.4	PROTECTION

A.	Protect installed equipment enclosures from damage during construction.

END OF SECTION