Middle Atlantic Products, Inc.	January 2019

Phone	(973) 839-1011

Fax	(973) 839-1976

Website	middleatlantic.com

E-mail	info@middleatlantic.com

Product Guide Specification

Specifier Notes:  This product guide specification is written according to the Construction Specifications Institute (CSI) 3-Part Format, including MasterFormat, SectionFormat, and PageFormat, as described in The Project Resource Manual—CSI Manual of Practice.

The section must be carefully reviewed and edited by the Architect or Engineer to meet the requirements of the project and local building code.  Coordinate this section with other specification sections and the Drawings.  Delete all “Specifier Notes” when editing this section.

Section numbers and titles are from MasterFormat 2004 Edition.

SECTION 27 11 16

VIDEO EQUIPMENT ENCLOSURES

Specifier Notes:  This section covers Middle Atlantic Products, Inc. VMRK-54 19-Inch Video Enclosure.  Consult Middle Atlantic Products for assistance in editing this section for the specific application.

PART 1	GENERAL

1.1	SECTION INCLUDES

A.	Video equipment enclosures.

1.2	RELATED SECTIONS

Specifier Notes:  List sections with work directly related to this section.

A.

1.3	REFERENCES

Specifier Notes:  List standards referenced in this section, complete with designations and titles.  This article does not require compliance with standards, but is merely a listing of those used.

A.	ASCE 7 – Minimum Design Loads for Buildings and Other Structures.

B.	CBC – California Building Code.

C.	EIA/TIA 310D – Cabinets, Racks, Panels and Associated Equipment.

D.	IBC – International Building Code.

E.	ISO 9001:2000 – Quality Management Systems – Requirements.

F.	NFPA 5000 – Building Construction and Safety Code.

G.	UBC – Uniform Building Code.

H.	UL – Underwriters Laboratories.

1.4	SUBMITTALS

A.	Comply with Section 01 33 00 – Submittal Procedures.

B.	Product Data:  Submit manufacturer’s product data, including options.

C.	Warranty:  Submit manufacturer’s standard warranty.

1.5	QUALITY ASSURANCE

- Manufacturer’s Qualifications:  ISO 9001:2000 registered company.

- Conform to ISO 14025 and EN 15804 or ISO 21930 in the development of life cycle assessments (LCA) and Type III environmental product declarations (EPD).

1.6	DELIVERY, STORAGE, AND HANDLING

A.	Delivery:  Deliver materials to site in manufacturer’s original, unopened containers and packaging, with labels clearly identifying product name and manufacturer.

B.	Storage:  Store materials in clean, dry area indoors in accordance with manufacturer’s instructions.

C.	Handling:  Protect materials and finish during handling and installation to prevent damage.

1.7	WARRANTY

A.	Warranty Period:  Product lifetime.

PART 2	PRODUCTS

2.1	MANUFACTURER

A.	Middle Atlantic Products, Inc.  Phone (973) 839-1011.  Fax (973) 839-1976.  Website middleatlantic.com.  E-mail info@middleatlantic.com.

2.2	VIDEO EQUIPMENT ENCLOSURES

A.	Video Equipment Enclosures:  VMRK-54 19-Inch Video Enclosure.

1.	Model:  VMRK-54.

2.	Type:  19-inch, gangable equipment enclosure.

3.	Compliance:

a.	EIA/TIA 310D.

b.	Seismic Certified:  Seismic certified to 1997 UBC and 2001 CBC Seismic Zone 4 and 2000 IBC, 2003 IBC, 2002 ASCE Standard 7, and 2003 NFPA 5000 Seismic Use Group III lateral force requirements for protecting 600 pounds of essential equipment in upper floor installations when used with optional MRK-Z4 seismic floor anchor brackets with Ip value of 1.5.

4.	UL Listed:  US and Canada.

5.	Overall Dimensions:

a.	Height:  100.625 inches (2,555 mm).

b.	Width:  22 inches (558 mm).

c.	Depth:  31.40 inches (797 mm).

6.	Useable Height:  54 rackspaces.

7.	Construction:  Fully welded.

8.	Weight Capacity:  2,500 pounds.

9.	Materials:

a.	Top and Bottom:  14-gauge steel.

b.	Sides:  16-gauge steel.

c.	Structural Thickness:  11-gauge steel, where rackrail brackets are welded to sides.

d.	Internal Braces:  1/8-inch thick structural steel.

e.	Rear Door:  18-gauge steel, solid, latching.

10.	Finish of Structural Elements:  Black textured powder coat.

11.	Rackrail:

a.	Fully adjustable.

b.	11-gauge steel with tapped 10-32 mounting holes in universal EIA spacing.

c.	Finish:  Black e-coat.

d.	Rackspaces:  Numbered and bracketed.

12.	Removable Rear Knockout Panels:

a.	Top and Bottom:  1/2-inch, 3/4-inch, 1-inch, and 1-1/2-inch electrical knockouts.

b.	Top:  5/8-inch BNC knockouts for UHF/VHF antennas.

13.	Grounding and Bonding Stud:  1/4-20 by 1-inch threaded, installed in base.

2.3	OPTIONS

Specifier Notes:  Specify required options.  Delete options not required.  Consult Middle Atlantic Products for more information.

A.	Front Doors:  16-gauge steel, [solid]  [fully vented]  [plexi].

B.	Removable Keylocked Side Panels:  16-gauge steel, 2 panels per side, with recessed lift handles.

C.	Top Panels:  16-gauge steel, [solid]  [vented]  [accepts up to four 4-1/2-inch fans]  [accepts 10-inch fan]  [accepts 6-inch and 12-inch wide cable ladders]  [pagoda vented, adds 1.41 inches (36 mm) to top of enclosure].

D.	Additional Rail Kit:  54 space, 10-32 threaded, pair, includes hardware.

E.	Lacer Strip:  11-gauge steel, heavily perforated, 77 inches long.

F.	Vertical AC power strips.

G.	Top Rails:  13 spaces.

H.	Riser bases.

I.	Horizontal lacer bars.

J.	Seismic compliancy floor anchor brackets.

K.	Copper buss bar.

L.	Document pocket.

M.	Equipment mounting hardware.

N.	Ganging hardware.

O.	Leveling feet.

P.	Universal front doors.

Q.	Wrinkle touch-up paint.

PART 3	EXECUTION

3.1	EXAMINATION

A.	Examine areas to receive video equipment enclosures.

B.	Notify Architect of conditions that would adversely affect installation or subsequent use.

C.	Do not begin installation until unacceptable conditions are corrected.

3.2	INSTALLATION

A.	Install video equipment enclosures in accordance with manufacturer’s instructions at locations indicated on the Drawings.

B.	Install video equipment enclosures plumb, level, square, and secure.

3.3	ADJUSTING

A.	Adjust operating hardware to operate smoothly without binding.

B.	Repair minor damages to finish in accordance with manufacturer’s instructions and as approved by Architect.

3.4	PROTECTION

A.	Protect installed video equipment enclosures from damage during construction.

END OF SECTION