## Sheet1
According to:
|  | Siemens | Line Constant by Steffen Schmidt [p.p.s.]
SIEMENS -FORMEL UND TABELLENBUCH FUER STARKSTROM INGENIEURE
|  | conductor : |  | BLUEBIRD |  | 2156000 | cm | 2156 | MCM | 1.762 | dia[inches]
[6 empty] | R | 0.0105 | ohm/1000ft | a.c. 75oC
0.010479
|  | no.of parallel line |  | npar | 3
|  | total S transf. |  | Stran | 600 | MVA
|  | no.circuits per line |  | ncrc | 2
|  | no.cond.per bundle |  | nc | 1
|  |  |  | Dm | 6.3572 | m
|  | 0 |  | ULL | 138 | kV | required Ur
|  |  |  | Urreq | 79.6743 | kV
|  |  |  | SIL | 329.6176 | MVA
|  | miles= | 70 | length | 112 | km
|  |  |  | frq | 60 | HZ
| 600 | 1 |  | Sr | 600 | MVA
| conductor cross section |  |  | sq | 1092.4452 | mm^2 | 2156 | kcm
|  |  |  | Tamb | 25 | oC
|  |  |  | Tcond | 75 | oC
total resistance of all parallel lines |  |  |  | Rl | 0.0057299 | ohm/km |  | 29/sq*1.06*(228+Tcond)/(228+20)/nc/ncrc/npar
| conductor radius |  |  | rt | 22.3774 | mm |  | 0.881
distance between bundled conductors |  |  |  | dist | 400 | mm
equivalent radius of bundel |  |  |  | req | 22.3774 | 4475.48 |  | (rt*nc*(sag/2/SIN(PI()/nc)^(nc-1)))^(1/nc)
|  |  |  | µo | 0.0012566 | H/km
|  |  |  | µr | 1 | Al
total reactance of all parallel lines |  |  |  | Xl | 0.074133 | ohm/km |  | X1=f*µo*(µr/4/n+ln(dm/r)
| dielectric constant |  |  | εo | 8.854e-09 | F/km |  | 8.854 nF/km
|  |  |  | εr | 1 | Al
|  |  |  | Cap | 5.9085e-08 | F
|  |  |  | Ur | 79.6743371481684
|  |  | 2.5102 | Ir | 2.51021856169403
|  |  |  | p.f. | 1
|  |  |  | fi | 0
|  | check: |  | Srcalc | 600.000000000002
|  |  |  | Qr | 0
|  |  |  | Pr | 600
|  |  |  | RandX | 0.00572985853351079+0.0741327029027448i
|  |  |  | GandC | 0.00002227448393355i
|  |  |  | γ | 0.0000496237093562252+0.00128597442131953i
|  |  |  | gl | 0.00555785544789722+0.144029135187787i
|  | Zeq | 57.776 | Z | 57.7330736440805-2.22782756737549i
|  |  |  | chg | 0.989661007119914+0.000797732466026223i
|  |  |  | shg | 0.00550033618542643+0.143533902133394i
|  | 1.043 | 83.1043 | Us | 80.4503974836245+20.8341101219146i
|  |  |  | Is | 2.48421250244818+0.200083926906699i
|  |  |  | Ss | 612.073361467635+106.978576177542i
|  |  |  | Qs | 106.9786
| total reactive losses |  | MVAr | Qsloss | 106.9786
|  |  |  | Ps | 612.0734
| active line losses |  | MW | Ploss | 12.0734
|  |  | 0.04305 | VD | 4.305 | %
Dm calculation
[12 empty] | Dm= | (d12*d23*d31*d1ii*d2III*d3I/(d1I*d2II*d3III))^(1/3)
2*3*240+1*50ACSR
X1=0.424
[14 empty] | horiz. | vert.
[13 empty] | d12 | 0.8 | 4.4 | 4.4721
[13 empty] | d23 | 0.8 | 4.1 | 4.1773
[13 empty] | d31 | 0 | 8.5 | 8.5
[13 empty] | d1II | 10 | 4.4 | 10.9252
[13 empty] | d2III | 10 | 4.1 | 10.8079
[13 empty] | d3I | 9.2 | 8.5 | 12.5256 | 234854.3928
[13 empty] | d1I | 9.2 | 0 | 9.2
[13 empty] | d2II | 10.8 | 0 | 10.8
[13 empty] | d3III | 9.2 | 0 | 9.2 | 914.112
[16 empty] | Dm= | 6.3572
1
2
3
I
II
III