## KercelXLS
THIS PROGRAM IS PREPARED ACC. TO -
DESIGN OF SWITCHYARD GROUNDING SYSTEMS
USING MULTIPLE GRIDS-by Stephen W. Kercel -
IEEE TRANS. ON POWER APP.&SYST.S
VOL PAS-100,NO 3 March 1981
ADDED:
CURRENT SHARING RATE BETWEEN DIFFERENT GRIDS
ACCORDING TO ME:
1) Constant Distribution of Current [A/m]
2) Constant Potential throughout the entire Grid
3) The current per meter grounding cable is
direct proportional to the distance from the center | Remarks
[As in"OPTIMUM"] | SEE "TypicalShortCircuit.xls"
INPUT DATA: | Parameter | Value | U/M
TOTAL Igrid= | Igrid | 28.4 | kA
Fault Clearing Time | T | 0.25
Frequence | F | 60
NO OF GRIDS(2-3)= | NOG | 2
DISTANCE BET. GRIDS NO 1& 2 [m]= DSAB | DSAB | 894
DISTANCE BET. GRIDS NO 2& 3 [m]= DSBC | DSBC | 400
DISTANCE BET. GRIDS NO 1& 3 [m]= DSAC | DSAC | 806
GRID NO.1 [A]
A=LONG SIDE OF A GRID= | AA | 800
B=SHORT SIDE OF A GRID= | BA | 500
DISTANCE BTW.CONN.(DA)[M]= | DAA | 35
DISTANCE BTW.CONN.(DB)[M]= | DBA | 35
RO[OHM.M]= | ROA | 75
CONDUCTOR BURING DEPTH[M]= | CBA | 0.8
CONDUCTOR DIA[MM]= | DIA | 12.7
GRID NO.2 [B]
A=LONG SIDE OF B GRID= | AB | 200
B=SHORT SIDE OF B GRID= | BB | 1100
DISTANCE BTW.CONN.(DA)[M]= | DAB | 40
DISTANCE BTW.CONN.(DB)[M]= | DBB | 70
RO[OHM.M]= | ROB | 200
CONDUCTOR BURING DEPTH[M]= | CBB | 0.8
CONDUCTOR DIA[MM]= | DIB | 12.7
GRID NO.3 [C]
A=LONG SIDE OF C GRID= | AC | 600
B=SHORT SIDE OF C GRID= | BC | 1100
DISTANCE BTW.CONN.(DA)[M]= | DAC | 75
DISTANCE BTW.CONN.(DB)[M]= | DBC | 300
RO[OHM.M]= | ROC | 200
CONDUCTOR BURING DEPTH[M]= | CBC | 0.8
CONDUCTOR DIA[MM]= | DIC | 12.7
CALCULATED DATA: | A | 0.106
X/R= | XperR | 10
| TA | 0.026526
| FUN | 0.99992
| DCR | 1.0517
NAA = INT(AA/ DAA) + 1 | NAA | 23
NAB = INT(AB/ DAB) + 1 | NAB | 6
NAC = INT(AC/ DAC) + 1 | NAC | 9
NBA = INT(BA/ DBA) + 1 | NBA | 15
NBB = INT(BB/ DBB) + 1 | NBB | 16
NBC = INT(BC/ DBC) + 1 | NBC | 4
LA = NAA * BA + NBA * AA | LA | 23500
LB = NAB * BB + NBB * AB | LB | 9800
LC = NAC * BC + NBC * AC | LC | 12300
LTOT=LA+LB+LC | LTOT | 45600
ROM=MAX(ROA,ROB) | ROM | 200
RAB = ROM / 2 / PI() / DSAB | RAB | 0.035605
RON=MAX(ROC,ROB) | RON | 200
RBC = RON / 2 / PI() / DSBC | RBC | 0.079577
ROP=MAX(ROA,ROC) | ROP | 200
RAC= ROP / 2 / PI() / DSAC | RAC | 0.039493
GRID NO.1 [A]
BAA = (BA + SQRT(AA ^ 2 + BA ^ 2)) / AA | BAA | 1.8042
BBA = (AA + SQRT(AA ^ 2 + BA ^ 2)) / BA | BBA | 3.4868
BCA= (AA ^ 2 + BA ^ 2) * SQRT(AA ^ 2 + BA ^ 2) / 3 / AA ^ 2 / BA ^ 2 | BCA | 0.0017492
KAA=SQRT(AA*BA)/2*1.84*(LN(BAA)/BA+LN(BBA)/AA+BA/3/AA^2+AA/3/BA^2-BCA) | KAA | 1.3496
SQAB = SQRT(BA ^ 2 + AA ^ 2 / 4) | SQAB | 640.3124
BDA = (BA + SQAB) * 2 /AA | BDA | 2.8508
BEA = (AA/ 2 + SQAB) / (SQAB - AA / 2) | BEA | 4.329
KBA=LN(4*(AA+BA)/AA)+2*KAA*(AA+BA)/SQRT(AA*BA)-LN(BDA)-LN(BEA)/2 | KBA | 5.6395
SAB=AA*BA | SAB | 400000
APA = SQRT(2 * CBA * DIA / 1000) | APA | 0.14255
RA = ROA / PI() / LA * (LN(2 * LA / APA) + KAA * LA / SQRT(SAB) - KBA) | RA | 0.05812
GRID NO.2 [B]
BAB = (BB + SQRT(AB ^ 2 + BB ^ 2)) / AB | BAB | 11.0902
BBB = (AB + SQRT(AB ^ 2 + BB ^ 2)) / BB | BBB | 1.1982
BCB= (AB ^ 2 + BB ^ 2) * SQRT(AB ^ 2 + BB ^ 2) / 3 / AB ^ 2 / BB ^ 2 | BCB | 0.0096249
KAB=SQRT(AB*BB)/2*1.84*(LN(BAB)/BB+LN(BBB)/AB+BB/3/AB^2+AB/3/BB^2-BCB) | KAB | 1.16
SQBB = SQRT(BB ^ 2 + AB ^ 2 / 4) | SQBB | 1104.5361
BDB = (BB + SQBB) * 2 /AB | BDB | 22.0454
BEB = (AB/ 2 + SQBB) / (SQBB - AB / 2) | BEB | 1.1991
KBB=LN(4*(AB+BB)/AB)+2*KAB*(AB+BB)/SQRT(AB*BB)-LN(BDB)-LN(BEB)/2 | KBB | 6.5046
SBB=AB*BB | SBB | 220000
APB = SQRT(2 * CBB * DIB / 1000) | APB | 0.14255
RB = ROB / PI() / LB * (LN(2 * LB / APB) + KAB * LB / SQRT(SBB) - KBB) | RB | 0.19205
GRID NO.3 [C]
BAC = (BC + SQRT(AC ^ 2 + BC ^ 2)) / AC | BAC | 3.9217
BBC = (AC + SQRT(AC ^ 2 + BC ^ 2)) / BC | BBC | 1.6845
BCC= (AC ^ 2 + BC ^ 2) * SQRT(AC ^ 2 + BC ^ 2) / 3 / AC ^ 2 / BC ^ 2 | BCC | 0.0015054
KAC=SQRT(AC*BC)/2*1.84*(LN(BAC)/BC+LN(BBC)/AC+BC/3/AC^2+AC/3/BC^2-BCC) | KAC | 1.3378
SQCB = SQRT(BC ^ 2 + AC ^ 2 / 4) | SQCB | 1140.1754
BDC = (BC + SQCB) * 2 /AC | BDC | 7.4673
BEC = (AC/ 2 + SQCB) / (SQCB - AC / 2) | BEC | 1.7141
KBC=LN(4*(AC+BC)/AC)+2*KAC*(AC+BC)/SQRT(AC*BC)-LN(BDC)-LN(BEC)/2 | KBC | 5.7465
SCB=AC*BC | SCB | 660000
APC = SQRT(2 * CBC * DIC / 1000) | APC | 0.14255
RC = ROC / PI() / LC* (LN(2 * LC / APC) + KAC * LC / SQRT(SCB) - KBC) | RC | 0.1375
TWO GRIDS
RTOT = (RA * RB - RAB ^ 2) / (RA + RB - 2 * RAB) | RTOT | 0.055288
GRP=RTOT*Igrid | GRP | 1.6514
THREE GRIDS
HOP = RA * RB * RC + 2 * RAB * RAC * RBC - RA * RBC ^ 2 - RB * RAC ^ 2 - RC * RAB ^ 2 | HOP | 0.00091671
DA = RA * RB + RA * RC + RB * RC | DA | 0.045562
DB = - (RBC ^ 2 + RAC^ 2 + RAB ^ 2) | DB | -0.00916
DC = (RAB * RBC + RBC * RAC+ RAB * RAC - RAB * RC - RAB * RB - RBC * RA) | DC | -0.0089767
D=DA+DB+2*DC | D | 0.018448
RTQT = HOP / D | RTQT | 0.049691
GRQ=RTQT*Igrid | GRQ | 1.4842
1) Constant Distribution of Current [A/m]
IAarea=Igrid/LTOT*LA | IA | 14.636
IBarea=Igrid/LTOT*LB | IB | 6.1035
ICarea=Igrid/LTOT*LC | IC | 7.6605
2)Same grid potential rise | I1TOT | 28.4
IAarea=GRP[GRQ]/RA/KRED | IAP | 15.4606 | 105.6% | IA
IBarea=GRP[GRQ]/RB/KRED | IBP | 4.6787 | 76.66% | IB
ICarea=GRP[GRQ]/RC/KRED | ICP | 6.535 | 85.31% | IC
| I2TOT | 26.6743 | 93.92%
KRED=FIRSTSUM(IA+IB+IC)/Igrid | KRED | 1.6517
2a)same grid pot.calculated as per 665-1995 | SUPR | 1280000
SUPR=AA*BA+AB*BB+AC*BC | SR | 78.5
Zg=SR*(1/LTOT+1/SQRT(20*SUPR)*(1+1/(1+h*sqrt(20/SUPR)) | ZG | 0.032702 | 65.81% | RTQT
ZG=1/(1/ZA+1/ZB+1/ZC) | ZGA | 0.03277
NEW GRP AS PER IEEE Std 665-1995 | GRPN | 0.97678 | KV
ZA=ROA*(1/LA+1/SQRT(20*AA*BA)*(1+1/(1+CBA*SQRT(20/AA/BA)) | ZA | 0.056075 | 96.48% | RA
IAS=ZG*Igrid/ZA | IAS | 16.5625 | 107.1% | IAP
ZB=ROB*(1/LB+1/SQRT(20*AB*BB)*(1+1/(1+CBA*SQRT(20/AB/BB))) | ZB | 0.21038 | 109.5% | RB
| IBS | 4.4146 | 94.36% | IBP
ZC=ROC*(1/LC+1/SQRT(20*AC*BC)*(1+1/(1+CBA*SQRT(20/AC/BC))) | ZC | 0.12612 | 91.72% | RC
| ICS | 7.3643 | 112.7% | ICP
| SUMM | 28.3415