Sentinel Installation Troubleshooting 2

Hi Daniel,

The S-Box and your PC communicate because the communication via TCP/IP

was established .

If your sentinels are flashing red two times and green two times?

(Embedded image moved to file: pic18467.gif)

If yes , That means that all the id of the sentinel were reset  :

Unplug all the sentinels

Do the procedure on user guide Chapiter 5.2.4.

(Embedded image moved to file: pic06334.gif)

(Embedded image moved to file: pic26500.gif)

If no,  but the sentinels are flashing green =>

(Embedded image moved to file: pic19169.gif)

Plug all the sentinels

Do the procedure below

(Embedded image moved to file: pic15724.gif)

If after you have the problem yet , you must check some points below :

Please check the external power supply 24V DC is connected to the Bus

converter?

Please check that the S-BUS converter is connected like the schematic

below please ?

(Embedded image moved to file: pic11478.gif)

I wait your feedback please

Best Regards

EL HAJJI Nacim